## 2024
TAKORADI INTERNATIONAL COMPANY
I&C DEPARTMENT CALIBRATION SHEET
PRESSURE TRANSMITTER CALIBRATION REPORT
Manufacturer: | ROSEMOUNT |  |  | Description: | LP INLET PRESS. TRANSMITTER
Model No.: | 2051CG4A02A1AH2B |  |  | Tag No.: | 30MAC10CP001A
S/N: | 116992 |  |  | Range: | 0 - 200
|  |  |  | Unit: | PSI
|  |  |  | Location: | STG
Span | Standard pressure | Desired Output | Transmitter Output
|  |  | AS FOUND |  | AS LEFT
|  |  | Actual Reading | Error | Actual Reading | Error
% | PSI | PSI | mA | % | mA | %
0% | 0 | 0 | 4 | 0 | 4 | 0
25% | 50 | 50 | 12 | 0 | 12 | 0
50% | 100 | 100 | 16 | 0 | 16 | 0
75% | 150 | 150 | 18 | 0 | 18 | 0
100% | 200 | 200 | 20 | 0 | 20 | 0
TEST EQUIPMENT
Description | Reference Pressure Gauge
Manufacturer | Fluke
Model No | 2700G
Serial No.: | 4981657
Cal Due. | 2024-08-22
REMARKS: Calibrated during STG outage. Calibration successful
NAME |  | I&C DEPARTMENT
CALIBRATION DATE |  | 2023-01-10
NEXT CAL. DUE DATE |  | 2024-07-10